Gold Mountain CSD Field Report

For work done in August 2020

By Skyler Allingham

Water Distribution System:

- Booster Station#1

Work schedule to be determined the Wildfires are causing delays. The new access road will be installed by McGarr Excavation at Booster Station #1.  There is a cross connection between the Golf course irrigation system and the CSD potable water system. The cross connection will be disconnected, and the two systems separated just outside the building to prevent contamination.

- Well #29 Offline Until repair is made.

Well #29 air problem have been determined to be coming from the aquifer and this continually causing cloudy water for this reason we are taking #29 offline. The cloudy water in system has no heath impact. Working with Shaw Engineering and Plumas Geo-Hydrology we have found a solution to off gas the water. By adding a 14000 gal water tank at #29 and booster pump to inject the water into the system. Estimates are coming in around 55k

- The Air relief valve project or A.R.V.P.

Eagle Nest and Double Eagle A.R.V has been repaired. We found a missing ARV on Red Sky. For the rest of the system we will look for fix or replace the broken ones and add goose necks in entire water system to prevent contamination.

- New Water Wells Update #36 & #37

### Well 36 Sunburst is still awaiting the seed shipment after seeding and pine needle mulch remediation will be complete.

### Well 37 Deer Trail   Casing and seal have been completed. The next step is to

### install the utility lines and build the building.

- Well 17 Building maintenance and Bird Damage

The Building has been resided with concrete siding and repainted

this should prevent further weathering and pest damage.

Sewer Transmission System:

- Septic tank inspection program

The 2020 Septic tank inspection program is moving along well ½ of the tanks in the system are done.

- Falling Water Dosing station

The main gasket on the dosing pump. We replaced the gasket with an EDPM style this will increase the life of system.

.